## CEBAF-UITF
Initial vital statistics: |  |  | Blue boxes are calculated based on yellow entry.
25 | cubic feet for UITF or CEBAF Glassman |  |  |  |  | volume in liters = |  |  | 707.92
The system is pumped to a vacuum to prepare for refill with SF6. The final vacuum level is entered below.
Enter final vacuum in Torr |  |  |  | 10 |  | Calculated pressure in atmospheres = |  |  |  | 0.013158 |  | Gauge reading in inches of mercury = |  | 29.5263
Number of moles of any gas (n) in the tank volume when pumped to vacuum level entered.
T (25C) = 298 Kelvin
R=0.08206L-atm/k-mol (Ideal Gas Law constant)
PV=nRT, So n=PV/RT |  |  | 0.38091 | moles
Molecular weight of air = 29g/mol |  |  |  | Therefore each pumpdown of the tank from air, leaves | [5 empty] | 11.0464 | grams of air to mix with the SF6 |  | 0.024353
Molecular weight of SF6 = 146g/mol |  |  |  | Therefore each pumpdown of the tank from SF6, leaves behind | [6 empty] | 55.6129 | grams of SF6 to be vented to air when the tank opens
[11 empty] | 0.12261 | pounds of SF6 (liquid or vapor)
System pressurization calculations:
How many moles of gas are contained in the system when pressurized to | [6 empty] | 60 | psig?
60 | psig is | 5.0827 | atmospheres
n= PV/RT = |  | 147.1413 | moles of gas |  | When this gas is pure SF6, it weighs |  |  |  | 21482.6307 | grams | 47.361 | pounds
[5 empty] | When this gas is pure air, it weighs |  |  |  | 4267.0979 | grams | 9.4073 | pounds
SF6 gas management table for UITF and CEBAF Glassman tanks. | [6 empty] | Aluminum Cylinders hold 75lbs of SF6. They have an empty weight of 49.5lbs
which means that when filled with SF6 to their normal maximum volume, the cylinder will weigh 125lbs.
TANK PSI |  | LBS mass of SF6 |  | Pressure in Atm |  | LBS mass of SF6
60 |  | 47.361 |  | 5.0827 |  | 47.361 |  | 0.63405 |  | 1 PSI difference is equivaelnt to 0.634 lbs mass of SF6 difference
59 |  | 46.727 |  | 5.0147 |  | 46.727
58 |  | 46.0929 |  | 4.9467 |  | 46.0929
57 |  | 45.4589 |  | 4.8786 |  | 45.4589
56 |  | 44.8248 |  | 4.8106 |  | 44.8248
55 |  | 44.1908 |  | 4.7425 |  | 44.1908 |  | 3.1703
54 |  | 43.5567 |  | 4.6745 |  | 43.5567 |  | 5
53 |  | 42.9227 |  | 4.6064 |  | 42.9227
52 |  | 42.2886 |  | 4.5384 |  | 42.2886
51 |  | 41.6546 |  | 4.4703 |  | 41.6546
50 |  | 41.0205 |  | 4.4023 |  | 41.0205
49 |  | 40.3865 |  | 4.3342 |  | 40.3865
48 |  | 39.7524 |  | 4.2662 |  | 39.7524
47 |  | 39.1184 |  | 4.1981 |  | 39.1184
46 |  | 38.4843 |  | 4.1301 |  | 38.4843
45 |  | 37.8503 |  | 4.0621 |  | 37.8503
44 |  | 37.2162 |  | 3.994 |  | 37.2162
43 |  | 36.5822 |  | 3.926 |  | 36.5822
42 |  | 35.9481 |  | 3.8579 |  | 35.9481
41 |  | 35.3141 |  | 3.7899 |  | 35.3141
40 |  | 34.68 |  | 3.7218 |  | 34.68
39 |  | 34.046 |  | 3.6538 |  | 34.046
38 |  | 33.4119 |  | 3.5857 |  | 33.4119
37 |  | 32.7779 |  | 3.5177 |  | 32.7779
36 |  | 32.1438 |  | 3.4496 |  | 32.1438
35 |  | 31.5098 |  | 3.3816 |  | 31.5098
34 |  | 30.8757 |  | 3.3136 |  | 30.8757
33 |  | 30.2417 |  | 3.2455 |  | 30.2417
32 |  | 29.6076 |  | 3.1775 |  | 29.6076
31 |  | 28.9736 |  | 3.1094 |  | 28.9736
30 |  | 28.3395 |  | 3.0414 |  | 28.3395
29 |  | 27.7055 |  | 2.9733 |  | 27.7055
28 |  | 27.0714 |  | 2.9053 |  | 27.0714
27 |  | 26.4374 |  | 2.8372 |  | 26.4374
26 |  | 25.8033 |  | 2.7692 |  | 25.8033
25 |  | 25.1693 |  | 2.7011 |  | 25.1693
24 |  | 24.5352 |  | 2.6331 |  | 24.5352
23 |  | 23.9012 |  | 2.5651 |  | 23.9012
22 |  | 23.2671 |  | 2.497 |  | 23.2671
21 |  | 22.6331 |  | 2.429 |  | 22.6331
20 |  | 21.999 |  | 2.3609 |  | 21.999
19 |  | 21.365 |  | 2.2929 |  | 21.365
18 |  | 20.7309 |  | 2.2248 |  | 20.7309
17 |  | 20.0969 |  | 2.1568 |  | 20.0969
16 |  | 19.4628 |  | 2.0887 |  | 19.4628
15 |  | 18.8288 |  | 2.0207 |  | 18.8288
14 |  | 18.1947 |  | 1.9526 |  | 18.1947
13 |  | 17.5607 |  | 1.8846 |  | 17.5607
12 |  | 16.9266 |  | 1.8165 |  | 16.9266
11 |  | 16.2926 |  | 1.7485 |  | 16.2926
10 |  | 15.6585 |  | 1.6805 |  | 15.6585
9 |  | 15.0245 |  | 1.6124 |  | 15.0245
8 |  | 14.3904 |  | 1.5444 |  | 14.3904 | [8 empty] | Inches of HG vacuum
7 |  | 13.7564 |  | 1.4763 |  | 13.7564
6 |  | 13.1223 |  | 1.4083 |  | 13.1223
5 |  | 12.4883 |  | 1.3402 |  | 12.4883
4 |  | 11.8542 |  | 1.2722 |  | 11.8542
3 |  | 11.2202 |  | 1.2041 |  | 11.2202
2 |  | 10.5861 |  | 1.1361 |  | 10.5861
1 |  | 9.9521 |  | 1.068 |  | 9.9521
0 |  | 9.318 |  | 1 |  | 9.318
" vacuum below this line
0 |  | 9.318 |  | 1 |  | 9.318
1 |  | 9.0066 |  | 0.96658 |  | 9.0062
2 |  | 8.6951 |  | 0.93316 |  | 8.6948
3 |  | 8.3837 |  | 0.89973 |  | 8.3834
4 |  | 8.0723 |  | 0.86631 |  | 8.072
5 |  | 7.7609 |  | 0.83289 |  | 7.7605
6 |  | 7.4494 |  | 0.79947 |  | 7.4491
7 |  | 7.138 |  | 0.76604 |  | 7.1377
8 |  | 6.8266 |  | 0.73262 |  | 6.8263
9 |  | 6.5151 |  | 0.6992 |  | 6.5149
10 |  | 6.2037 |  | 0.66578 |  | 6.2034
11 |  | 5.8923 |  | 0.63235 |  | 5.892
12 |  | 5.5808 |  | 0.59893 |  | 5.5806
13 |  | 5.2694 |  | 0.56551 |  | 5.2692
14 |  | 4.958 |  | 0.53209 |  | 4.9578
15 |  | 4.6465 |  | 0.49866 |  | 4.6464
16 |  | 4.3351 |  | 0.46524 |  | 4.3349
17 |  | 4.0237 |  | 0.43182 |  | 4.0235
18 |  | 3.7123 |  | 0.3984 |  | 3.7121
19 |  | 3.4008 |  | 0.36497 |  | 3.4007
20 |  | 3.0894 |  | 0.33155 |  | 3.0893
21 |  | 2.778 |  | 0.29813 |  | 2.7778
22 |  | 2.4665 |  | 0.26471 |  | 2.4664
23 |  | 2.1551 |  | 0.23128 |  | 2.155
24 |  | 1.8437 |  | 0.19786 |  | 1.8436
25 |  | 1.5322 |  | 0.16444 |  | 1.5322
26 |  | 1.2208 |  | 0.13102 |  | 1.2208
27 |  | 0.90938 |  | 0.097594 |  | 0.90934
28 |  | 0.59795 |  | 0.064171 |  | 0.59792
29 |  | 0.28652 |  | 0.030749 |  | 0.2865
29.92 |  | 0 |  | 0

## GTS
Initial vital statistics: |  |  | Blue boxes are calculated based on yellow entry.
130 | cubic feet for GTS Glassman |  |  |  |  | volume in liters = |  |  | 3681.184
The system is pumped to a vacuum to prepare for refill with SF6. The final vacuum level is entered below.
Enter final vacuum in Torr |  |  |  | 10 |  | Calculated pressure in atmospheres = |  |  |  | 0.013158 |  | Gauge reading in inches of mercury = |  | 29.5263
Number of moles of any gas (n) in the tank volume when pumped to vacuum level entered.
T (25C) = 298 Kelvin
R=0.08206L-atm/k-mol (Ideal Gas Law constant)
PV=nRT, So n=PV/RT |  |  | 1.9807 | moles
Molecular weight of air = 29g/mol |  |  |  | Therefore each pumpdown of the tank from air, leaves | [5 empty] | 57.4413 | grams of air to mix with the SF6 |  | 0.12664
Molecular weight of SF6 = 146g/mol |  |  |  | Therefore each pumpdown of the tank from SF6, leaves behind | [6 empty] | 289.1872 | grams of SF6 to be vented to air when the tank opens
[11 empty] | 0.63755 | pounds of SF6 (liquid or vapor)
System pressurization calculations:
How many moles of gas are contained in the system when pressurized to | [6 empty] | 0 | psig?
0 | psig is | 1 | atmospheres
n= PV/RT = |  | 150.5358 | moles of gas |  | When this gas is pure SF6, it weighs |  |  |  | 21978.2245 | grams | 48.4536 | pounds
[5 empty] | When this gas is pure air, it weighs |  |  |  | 4365.5377 | grams | 9.6244 | pounds
SF6 gas management table for UITF and CEBAF Glassman tanks.
Aluminum Cylinders hold 75lbs of SF6. They have an empty weight of 49.5lbs
TANK PSI |  | LBS mass of SF6 |  | Pressure in Atm |  |  | which means that when filled with SF6 to their normal maximum volume, the cylinder will weigh 125lbs.
15 |  | 97.9096 |  | 2.0207
14 |  | 94.6125 |  | 1.9526
13 |  | 91.3154 |  | 1.8846
12 |  | 88.0184 |  | 1.8165
11 |  | 84.7213 |  | 1.7485
10 |  | 81.4243 |  | 1.6805
9 |  | 78.1272 |  | 1.6124
8 |  | 74.8301 |  | 1.5444
7 |  | 71.5331 |  | 1.4763
6 |  | 68.236 |  | 1.4083
5 |  | 64.9389 |  | 1.3402
4 |  | 61.6419 |  | 1.2722
3 |  | 58.3448 |  | 1.2041
2 |  | 55.0478 |  | 1.1361
1 |  | 51.7507 |  | 1.068
0 |  | 48.4536 |  | 1
" vacuum below this line
0 |  | 48.4536 |  | 1
1 |  | 46.8342 |  | 0.96658
2 |  | 45.2148 |  | 0.93316
3 |  | 43.5953 |  | 0.89973
4 |  | 41.9759 |  | 0.86631
5 |  | 40.3564 |  | 0.83289
6 |  | 38.737 |  | 0.79947
7 |  | 37.1176 |  | 0.76604
8 |  | 35.4981 |  | 0.73262
9 |  | 33.8787 |  | 0.6992
10 |  | 32.2592 |  | 0.66578
11 |  | 30.6398 |  | 0.63235
12 |  | 29.0204 |  | 0.59893
13 |  | 27.4009 |  | 0.56551
14 |  | 25.7815 |  | 0.53209
15 |  | 24.162 |  | 0.49866
16 |  | 22.5426 |  | 0.46524
17 |  | 20.9232 |  | 0.43182
18 |  | 19.3037 |  | 0.3984
19 |  | 17.6843 |  | 0.36497
20 |  | 16.0648 |  | 0.33155
21 |  | 14.4454 |  | 0.29813
22 |  | 12.826 |  | 0.26471
23 |  | 11.2065 |  | 0.23128
24 |  | 9.5871 |  | 0.19786
25 |  | 7.9676 |  | 0.16444
26 |  | 6.3482 |  | 0.13102
27 |  | 4.7288 |  | 0.097594
28 |  | 3.1093 |  | 0.064171
29 |  | 1.4899 |  | 0.030749
29.52 |  | 0.64778 |  | 0.013369
Inches of HG vacuum

## LERF-FEL
Initial vital statistics: |  |  | Blue boxes are calculated based on yellow entry.
236 | cubic feet for FEL Glassman |  |  |  |  | volume in liters = |  |  | 6682.7648
The system is pumped to a vacuum to prepare for refill with SF6. The final vacuum level is entered below.
Enter final vacuum in Torr |  |  |  | 10 |  | Calculated pressure in atmospheres = |  |  |  | 0.013158 |  | Gauge reading in inches of mercury = |  | 29.5263
Number of moles of any gas (n) in the tank volume when pumped to vacuum level entered.
T (25C) = 298 Kelvin
R=0.08206L-atm/k-mol (Ideal Gas Law constant)
PV=nRT, So n=PV/RT |  |  | 3.5958 | moles
Molecular weight of air = 29g/mol |  |  |  | Therefore each pumpdown of the tank from air, leaves | [5 empty] | 104.278 | grams of air to mix with the SF6 |  | 0.22989
Molecular weight of SF6 = 146g/mol |  |  |  | Therefore each pumpdown of the tank from SF6, leaves behind | [6 empty] | 524.9859 | grams of SF6 to be vented to air when the tank opens
[11 empty] | 1.1574 | pounds of SF6 (liquid or vapor)
System pressurization calculations:
How many moles of gas are contained in the system when pressurized to | [6 empty] | 10 | psig?
10 | psig is | 1.6805 | atmospheres
n= PV/RT = |  | 459.2359 | moles of gas |  | When this gas is pure SF6, it weighs |  |  |  | 67048.4479 | grams | 147.8163 | pounds
[5 empty] | When this gas is pure air, it weighs |  |  |  | 13317.8424 | grams | 29.3608 | pounds
SF6 gas management table for UITF and CEBAF Glassman tanks.
Aluminum Cylinders hold 75lbs of SF6. They have an empty weight of 49.5lbs
TANK PSI |  | LBS mass of SF6 |  | Pressure in Atm |  |  | which means that when filled with SF6 to their normal maximum volume, the cylinder will weigh 125lbs.
15 |  | 177.7435 |  | 2.0207
14 |  | 171.7581 |  | 1.9526
13 |  | 165.7727 |  | 1.8846
12 |  | 159.7872 |  | 1.8165
11 |  | 153.8018 |  | 1.7485
10 |  | 147.8163 |  | 1.6805
9 |  | 141.8309 |  | 1.6124
8 |  | 135.8455 |  | 1.5444
7 |  | 129.86 |  | 1.4763
6 |  | 123.8746 |  | 1.4083
5 |  | 117.8892 |  | 1.3402
4 |  | 111.9037 |  | 1.2722
3 |  | 105.9183 |  | 1.2041
2 |  | 99.9329 |  | 1.1361
1 |  | 93.9474 |  | 1.068
0 |  | 87.962 |  | 1
" vacuum below this line
0 |  | 87.962 |  | 1
1 |  | 85.0221 |  | 0.96658
2 |  | 82.0822 |  | 0.93316
3 |  | 79.1423 |  | 0.89973
4 |  | 76.2024 |  | 0.86631
5 |  | 73.2625 |  | 0.83289
6 |  | 70.3225 |  | 0.79947
7 |  | 67.3826 |  | 0.76604
8 |  | 64.4427 |  | 0.73262
9 |  | 61.5028 |  | 0.6992
10 |  | 58.5629 |  | 0.66578
11 |  | 55.623 |  | 0.63235
12 |  | 52.6831 |  | 0.59893
13 |  | 49.7432 |  | 0.56551
14 |  | 46.8033 |  | 0.53209
15 |  | 43.8634 |  | 0.49866
16 |  | 40.9235 |  | 0.46524
17 |  | 37.9836 |  | 0.43182
18 |  | 35.0437 |  | 0.3984
19 |  | 32.1038 |  | 0.36497
20 |  | 29.1639 |  | 0.33155
21 |  | 26.224 |  | 0.29813
22 |  | 23.2841 |  | 0.26471
23 |  | 20.3441 |  | 0.23128
24 |  | 17.4042 |  | 0.19786
25 |  | 14.4643 |  | 0.16444
26 |  | 11.5244 |  | 0.13102
27 |  | 8.5845 |  | 0.097594
28 |  | 5.6446 |  | 0.064171
29 |  | 2.7047 |  | 0.030749
29.52 |  | 1.176 |  | 0.013369

## R30 pig
Initial vital statistics: |  |  | Blue boxes are calculated based on yellow entry.
Pig diameter | 12.75 | inches | 1.0625 | ft
Pig length | 34.5 | inches | 2.875 | ft
Pig volume | 2.5491
2.55 | cubic feet for R30 pig |  |  |  |  | volume in liters = |  |  | 72.2078
The system is pumped to a vacuum to prepare for refill with SF6. The final vacuum level is entered below.
Enter final vacuum in Torr |  |  |  | 10 |  | Calculated pressure in atmospheres = |  |  |  | 0.013158 |  | Gauge reading in inches of mercury = |  | 29.5263
Number of moles of any gas (n) in the tank volume when pumped to vacuum level entered.
T (25C) = 298 Kelvin
R=0.08206L-atm/k-mol (Ideal Gas Law constant)
PV=nRT, So n=PV/RT |  |  | 0.038853 | moles
Molecular weight of air = 29g/mol |  |  |  | Therefore each pumpdown of the tank from air, leaves | [5 empty] | 1.1267 | grams of air to mix with the SF6 |  | 0.002484
Molecular weight of SF6 = 146g/mol |  |  |  | Therefore each pumpdown of the tank from SF6, leaves behind | [6 empty] | 5.6725 | grams of SF6 to be vented to air when the tank opens
[11 empty] | 0.012506 | pounds of SF6 (liquid or vapor)
System pressurization calculations:
How many moles of gas are contained in the system when pressurized to | [6 empty] | 10 | psig?
10 | psig is | 1.6805 | atmospheres
n= PV/RT = |  | 4.9621 | moles of gas |  | When this gas is pure SF6, it weighs |  |  |  | 724.4642 | grams | 1.5972 | pounds
[5 empty] | When this gas is pure air, it weighs |  |  |  | 143.9004 | grams | 0.31725 | pounds
SF6 gas management table for UITF and CEBAF Glassman tanks.
Aluminum Cylinders hold 75lbs of SF6. They have an empty weight of 49.5lbs
TANK PSI |  | LBS mass of SF6 |  | Pressure in Atm |  |  | which means that when filled with SF6 to their normal maximum volume, the cylinder will weigh 125lbs.
15 |  | 1.9205 |  | 2.0207
14 |  | 1.8559 |  | 1.9526
13 |  | 1.7912 |  | 1.8846
12 |  | 1.7265 |  | 1.8165
11 |  | 1.6618 |  | 1.7485
10 |  | 1.5972 |  | 1.6805
9 |  | 1.5325 |  | 1.6124
8 |  | 1.4678 |  | 1.5444
7 |  | 1.4031 |  | 1.4763
6 |  | 1.3385 |  | 1.4083
5 |  | 1.2738 |  | 1.3402
4 |  | 1.2091 |  | 1.2722
3 |  | 1.1445 |  | 1.2041
2 |  | 1.0798 |  | 1.1361
1 |  | 1.0151 |  | 1.068
0 |  | 0.95044 |  | 1
" vacuum below this line
0 |  | 0.95044 |  | 1
1 |  | 0.91867 |  | 0.96658
2 |  | 0.8869 |  | 0.93316
3 |  | 0.85514 |  | 0.89973
4 |  | 0.82337 |  | 0.86631
5 |  | 0.79161 |  | 0.83289
6 |  | 0.75984 |  | 0.79947
7 |  | 0.72808 |  | 0.76604
8 |  | 0.69631 |  | 0.73262
9 |  | 0.66454 |  | 0.6992
10 |  | 0.63278 |  | 0.66578
11 |  | 0.60101 |  | 0.63235
12 |  | 0.56925 |  | 0.59893
13 |  | 0.53748 |  | 0.56551
14 |  | 0.50571 |  | 0.53209
15 |  | 0.47395 |  | 0.49866
16 |  | 0.44218 |  | 0.46524
17 |  | 0.41042 |  | 0.43182
18 |  | 0.37865 |  | 0.3984
19 |  | 0.34688 |  | 0.36497
20 |  | 0.31512 |  | 0.33155
21 |  | 0.28335 |  | 0.29813
22 |  | 0.25159 |  | 0.26471
23 |  | 0.21982 |  | 0.23128
24 |  | 0.18805 |  | 0.19786
25 |  | 0.15629 |  | 0.16444
26 |  | 0.12452 |  | 0.13102
27 |  | 0.092757 |  | 0.097594
28 |  | 0.060991 |  | 0.064171
29 |  | 0.029225 |  | 0.030749
29.52 |  | 0.012706 |  | 0.013369

## Inventory
SF6 system as of Nov 5 2021 | SF6 weight lbs | Pressure PSIG | Capacity SF6 lbs | Capacity cubic feet cf
CEBAF | 47 | 60 | 47 | 25
UITF | 44.5 | 55.5 | 47 | 25
LERF | 148 | 10 | 148 | 236
GTS | 82 | 10 | 82 | 130
R30 resistor tank | 1.5 | 10 | 1.6 | 2.5
GTS large K-bottle used | 110 | 2000 | 115 | 250
GTS large K-bottle used | 30 | 2000 | 115
CEBAF small K-bottle used | 20 | 2000
Traveling DILO cart | 0 | 720 | 75 x 2 = 150
Total | 483 |  | 555.6
109
6