## Slide 1: Conditioning resistor tank design (longer) with R30 connectors for 350kV based on John Hansknecht’s original design with R28 connectors (250kV)
Electrostatic POISSON and CST models by C.Hernandez-Garcia July-Aug 2020
SF6 breakdown curves from Malik and Qureshi IEEE Trans. Electr. Insul, Vol E1-13 No 3, June 1978

## Slide 2: Model includes HV cable plugs. All fields in MV/m for 400 kV
Resistor
The tank radius was designed by John to be 3 times the receptacle radius, this is the ideal ratio to minimize electric field at receptacle surface
Connector
R30 receptacle
Tank radius
Tank radius | Resistor (V,E) | Connector (V/E) | R30 (V,E)
6 cm | 400kV, 18 MV/m | 400kV, 22 MV/m | 58kV, 5 MV/m
16 cm design | 400kV, 10 MV/m | 400kV, 10 MV/m | 165kV, 3MV/m
26 cm | 400kV, 8.7 MV/m | 400kV, 9.3 MV/m | 185kV, 2.7 MV/m

## Slide 3: All fields in MV/m at 400 kV
20
8
10
8
5
Tanks are filled to 15 psig = 30 psi abs = 0.2 MPa
For uniform fields
184 kV/cm 18.4 MV/m @ 15 psig
153 kV/cm 15.3 MV/m @ 10 psig
~135 kV

## Slide 4: Breakdown in SF6
P = 15 psig (30 psi abs) = 206,843 Pa ~ 200 kPA
D = 16 cm – 4.5 cm = 11.5 cm
PxD = 2300 kPa cm
Breakdown = > 600 kV
Malik and Qureshi in IEEE Trans. Electr. Insul. Vol E1-13, No. 3, June 1978
P = 10 psig (25 psi abs)= 172,369 Pa ~ 172 kPA
D = 16 cm – 4.5 cm = 11.5 cm
PxD = 1978 kPa cm
Breakdown = > 600 kV

## Slide 5: The resistor tank was also modeled in CST, including details with rubber plug and its central conductor, and epoxy receptacle

## Slide 6: The potential was set to 400kV

## Slide 7: Potential from CST at 400 kV

## Slide 8: The electric field absolute is shown below

## Slide 9: The highest gradient (not surprisingly) is at the triple point junction

## Slide 10: Gradient at the triple point junction in the radial direction is about 6 MV/m,
and in the longitudinal direction is 35 MV/m

## Slide 11: The highest field in the radial direction is on the surface of the resistor connector, 10 MV/m

## Slide 12: The longitudinal component of the gradient at the triple point is what triggers arcing along the epoxy receptacle,.

## Slide 13: John has demonstrated this is not an issue at 400kV and 10 psig
Plugs are wet with NovaGard G661 silicone grease
Essex X-Ray R-30 Receptacles, Quantity 2 Part # S61006/C Essex X-Ray R-30 Cable, 6 feet.
https://wiki.jlab.org/ciswiki/index.php/Insulators,_Receptacle_connectors_and_cables:_drawings_and_inventories - HIGH_VOLTAGE_TESTS
Test start date 5-9-2012 Log entries in FGTS log (entries 1783796 and later) This test is presently ongoing.
“We have reached 400kV and it has been holding for many days. “ J. Hansknecth
07/14/20 Carlos got feedback from Jerry Goldlust (Dielectric Sciencies):
“The R30 receptacle and cable, at 10 psig are fine at 300 KVDC , with proper shielding of the triple point. Cutting ridges in the insulator should enhance the rating but not by much because of the non-linearity of the charge on the surface. As regards the cable plug itself, we have had the plug to 450 KVDC for ½ hour (with the receptacle in 20 psig of SF6).”

## Slide 14: We modeled John’s test setup in CST

## Slide 15: The models shows the gradient at the triple junction is lower than in the resistor tank, likely because the ball serves as a shield

## Slide 16: This is the longitudinal field comparison between the resistor tank and the ball test triple junction both at 400kV