## 16CH 16Bit DAC (Jlab)
UITF 16 Bit DAC CARD channel assignments
C1068 DAC CARD | IOCITFGUN | SLOT 5
Terminal breakout # | Channel number | EPICS ch name | Control item assigned | Remarks
1 | 1 | IGLK100HVSET | Glassman HV Voltage Setpoint | 0-10V makes 0 to 450KV
2 | 2 | IGLK100HVISET | Glassman HV Current Setpoint | 0-10V sets trip point 0 to 3mA
3 | 3
4 | 4
5 | 5
6 | 6
7 | 7
8 | 8
9 | 9
10 | 10
11 | 11
12 | 12
13 | 13
14 | 14
15 | 15
16 | 16
17 | N/C
18 | N/C
19 | N/C
20 | AGND
21 | AGND
22 | AGND
23 | AGND
24 | AGND
25 | AGND
26 | AGND
27 | AGND
28 | AGND
29 | AGND
30 | AGND
31 | AGND
32 | AGND
33 | AGND
34 | AGND
35 | AGND
36 | N/C
37 | N/C
NOTE: the DAC card is a 16 channel 16 bit DAC. Outputs should be set for 0 to +10vdc by taking J2-J17 to jumper 2-3 shorted position
and J18-J33 to the "ON" position
BASE address is SW7 OFF, SW8 OFF for 0XFFFF6600

## ADC XVME-566
UITF 16 Bit ADC CARD channel assignments
XVME-566 ADC card | IOCITFGUN | SLOT 7
Terminal breakout # | Channel number | EPICS ch name | Control item assigned | Remarks
1 | Channel 1 | IGLK100TANKPSI | Glassman Tank SF6 pressure | 2-10V = -15 to 100psi (4-20mA device on 500 ohms)
2 | Channel 9
3 | Ground
4 | Channel 2
5 | Channel 10
6 | Ground
7 | Channel 3
8 | Channel 11
9 | Ground
10 | Channel 12
11 | Channel 4
12 | Ground
13 | Channel 5
14 | Channel 13
15 | Ground
16 | Channel 14
17 | Channel 6
18 | Ground
19 | Channel 7
20 | Channel 15
21 | Ground
22 | Channel 16
23 | Channel 8
24 | Ground
25 | Channel 17
26 | Channel 25
27 | Ground
28 | Channel 26
29 | Channel 18
30 | Ground
31 | Channel 19
32 | Channel 27
33 | Ground
34 | Channel 28
35 | Channel 20
36 | Ground
37 | Channel 21
38 | Channel 29
39 | Ground
40 | Channel 30
41 | Channel 22
42 | Ground
43 | Channel 23
44 | Channel 31
45 | Ground
46 | Channel 32
47 | Channel 24
48 | Ground
49 | Gnd (ext trig, PDI)
50 | ext trigger.
Entire card is strapped for 0 to 10VDC input

## XVME244 in
UITF Digital Input channel assignments
XVME-244 Digital INPUTS | IOCITFGUN | SLOT 9
Terminal breakout # | Channel number | EPICS ch name | Control item assigned | Remarks |  | Wire color
| 1 | IGLK100DIOFLRDB.B0 | Status of Glassman HV | Hi= ON, Low= OFF
| 2 | IGLK100DIOFLRDB.B1 | Status of Glassman Pressure | Hi= Good, Low= bad (Glassman won't respond to Enable command when bad)
| 3 | IGLK100DIOFLRDB.B2 | Status of Glassman power | Hi= Good, Low= bad (Power supply has no power and PSS is likely the reason)
| 4 | IGLK100DIOFLRDB.B3 | Macropulse PSS (system B) |  |  | Yel
| 5 | IGLK100DIOFLRDB.B4 | Macropulse PSS (system A) | Hi= shutter open, Low = shutter closed |  | Org
| 6 | IGLK100DIOFLRDB.B5 | Macropulse chassis 18V OK | Hi= 18V passing through PSS |  | Grn
| 7 | IGLK100DIOFLRDB.B6 | Macropulse FSD OK |  |  | Blk
| 8 | IGLK100DIOFLRDB.B7 | Macropulse Bypass Active |  |  | Blu
| 9 | IGLK100DIOFLRDB.B8 | Macropulse BCM A OK |  |  | Brn
| 10 | IGLK100DIOFLRDB.B9 | Macropulse BCM B OK |  |  | Red
| 11 | IGLK100DIOFLRDB.B10 | Servo 1 retracted | Cave laser table power meter in/out servo |  | wht/org
| 12 | IGLK100DIOFLRDB.B11 | Servo 2 retracted |  |  | Org
| 13 | IGLK100DIOFLRDB.B12 | Servo 3 retracted | Cave laser table spiricon mirror in/out servo |  | wht/grn
| 14 | IGLK100DIOFLRDB.B13 | Servo 4 retracted |  |  | blu
| 15 | IGLK100DIOFLRDB.B14 | PSS B shutter (open when green)
| 16 | IGLK100DIOFLRDB.B15 | PSS A shutter (open when green
| 17 | IGLK100DIOFHRDB.B0 | Dipole Interlock OK | From Glassman pressure switch relay chassis J3
| 18 | IGLK100DIOFHRDB.B1 | Global Interlock OK | From Glassman pressure switch relay chassis J3
| 19 | IGLK100DIOFHRDB.B2 | LV Bias Probe retracted | From Glassman pressure switch relay chassis J3
| 20 | IGLK100DIOFHRDB.B3 | PSS A OK to Glassman remote | From Glassman pressure switch relay chassis J3
| 21 | IGLK100DIOFHRDB.B4 | PSS B OK to Glassman remote | From Glassman pressure switch relay chassis J3
| 22 | IGLK100DIOFHRDB.B5
| 23 | IGLK100DIOFHRDB.B6
| 24 | IGLK100DIOFHRDB.B7
| 25 | IGLK100DIOFHRDB.B8
| 26 | IGLK100DIOFHRDB.B9
| 27 | IGLK100DIOFHRDB.B10
| 28 | IGLK100DIOFHRDB.B11
| 29 | IGLK100DIOFHRDB.B12
| 30 | IGLK100DIOFHRDB.B13
| 31 | IGLK100DIOFHRDB.B14
| 32 | IGLK100DIOFHRDB.B15
A voltage input greater than 6VDC is registered as a TTL high. Card accepts up to 35VDC on inputs
https://www.acromag.com/sites/default/files/XVME-244_969a.pdf
white
| Note: All digital inputs are voltage sensing. |  |  |  | (needs >1.25mA for logic high)
Logic low is < 3vdc Logic high is > 10 vdc (up to 35vdc)
Test performed showed 24V through 13.74K energized input. Voltage drop across
the 17.74K was 17.22V. This left 6.56V into card at 1.25mA.

## XVME244 out
UITF Digital output channel assignments
XVME-244 Digital OUTPUTS | IOCITFGUN | SLOT 9
Terminal breakout # | Channel number | EPICS ch name | Control item assigned | Remarks | Wire color
| 1 | IGLK100DIOLWTB.B0 | Glassman HV Enable | Take High to energize Glassman
| 2 | IGLK100DIOLWTB.B1 | Actuate Servo 1 | Insert laser power meter servo on cave laser table | Wht/blu
| 3 | IGLK100DIOLWTB.B2 | Actuate Servo 2 |  | Grn
| 4 | IGLK100DIOLWTB.B3 | Actuate Servo 3 | Insert laser ccd camera mirror on cave laser table | wht/brn
| 5 | IGLK100DIOLWTB.B4 | Dead channel
| 6 | IGLK100DIOLWTB.B5 | Actuate Servo 4 |  | brn
| 7 | IGLK100DIOLWTB.B6
| 8 | IGLK100DIOLWTB.B7
| 9 | IGLK100DIOLWTB.B8
| 10 | IGLK100DIOLWTB.B9
| 11 | IGLK100DIOLWTB.B10
| 12 | IGLK100DIOLWTB.B11
| 13 | IGLK100DIOLWTB.B12
| 14 | IGLK100DIOLWTB.B13
| 15 | IGLK100DIOLWTB.B14
| 16 | IGLK100DIOLWTB.B15
| 17 | IGLK100DIOHWTB.B0
| 18 | IGLK100DIOHWTB.B1
| 19 | IGLK100DIOHWTB.B2
| 20 | IGLK100DIOHWTB.B3
| 21 | IGLK100DIOHWTB.B4
| 22 | IGLK100DIOHWTB.B5
| 23 | IGLK100DIOHWTB.B6
| 24 | IGLK100DIOHWTB.B7
| 25 | IGLK100DIOHWTB.B8
| 26 | IGLK100DIOHWTB.B9
| 27 | IGLK100DIOHWTB.B10
| 28 | IGLK100DIOHWTB.B11
| 29 | IGLK100DIOHWTB.B12
| 30 | IGLK100DIOHWTB.B13
| 31 | IGLK100DIOHWTB.B14
| 32 | IGLK100DIOHWTB.B15
All channels output 24VDC when activated with sufficient current to drive 24V relay coils
https://www.acromag.com/sites/default/files/XVME-244_969a.pdf
Note: Digital outputs are current sourcing 24vdc.
350mA Max

## Keithley 2000 DMM's
There are two Keithley 2000 DMM's in rack ITF21.
They are slaved off of the Ethernet to GPIB converter box in rack ITF16
Unit | Address | Purpose
Lefthand | 2 | Reads reported voltage of Glassman HVPS | 0-10.00000 volts = 0 to 450,000 volts
Righthand | 4 | Reads reported current of Glassman HVPS | 0-10.00000 volts = 0 to 3mA

## ethernet to GPIB loads
physical location of ethernet to GPIB is rack ITF16.
It is run by soft IOC | IOCITFGPIB1
Channel address | Item assigned | Location of item | Purpose
2 | Keithley 2000 DMM | ITF21 | Glassman voltage
4 | Keithley 2000 DMM | ITF21 | Glassman current
6 | Keithley Picoammeter | ITF04 | FC's/Dumps Multipurpose dependant on selection
7 | Keithley Picoammeter | ITF04 | CA ISLK302
8 | Keithley Picoammeter | ITF04 | A3 ISLK401
9 | Keithley Picoammeter | ITF04 | A4 ISLK403

## Serial Devices
All serial is passed through the Digiport 16 serial server
Rack ITF21 Network name itfdigips1 (Ip address 129.57.217.70 on itfsvcnet)
Channel |  | Protocol
1 | Kev region UHV ion pumps (running)
2 | MeV region UHV ion pumps (not presently installed)
3 | RadMon Chassis (used last week, but probably unplugged now as we swap guns)
4 | Spellman 225KV power supply (This was a work in progress for Mike. Not presently powered up)
5 | NM1830 Laser power meter for UITF laser table in Test Cave | 9600N81
6 | NM1830 Laser power meter for UITF laser table in laser room | 9600N81
7 | FAST SCOPE for Brock Cavity
8
9
10
11
12
13
14
15
16