## Slide 1
NPS cooling system
01/10/2021

## Slide 2
Total cooling (side crystals + side electronic)
Connected to 2 chillers
Reference plate
Support PMt plate
detail

## Slide 3
Front cooling (side crystals )
Connected to chiller n°1 Kodiak RC006G03BG3
2,3 GPM (Gallons / minute)
Inlet (copper tube D12, d10)
Return (copper tube D12, d10)
Divided in 2 branches ( copper tubes D10 ,d8)
Thirst branch cooling : 2 copper plates + half reference aluminum plate (cf slide 4)
Second branch cooling : 2 copper plates + half reference aluminum plate (cf slide 4)

## Slide 4
Front cooling (crystals )
Dividers:
1 inlet ;4 outlets
2 of them are used
Possibility if necessary to connect 2 other tubes

## Slide 5
Cooling edge of the reference plate (cut view)
1st branch
2nd branch

## Slide 6
Rear cooling (electronic )
Connected to chiller n°2 Kodiak RC011G03BG3
4,3 GPM (Gallons / minute)
2 heat exchangers Lytron 6320G3SB with funs 10 ’’
Inlet (copper tube D12, d10)
Return (copper tube D12, d10)
Divided in 2 branches ( copper tubes D10 ,d8)
Thirst branch cooling : Top heat exchanger + half support PMt aluminum plate (cf slide 6)
2nd branch cooling : Bottom heat exchanger + half support PMt aluminum plate (cf slide 7)

## Slide 7
Rear cooling (electronic )
2 heat exchangers Lytron 6320G3SB with funs 10 ’’
Return (copper tube D12, d10)
Inlet (copper tube D12, d10)
2nd branch
1st branch
Cut view

## Slide 8
Pictures
Copper tubes and brass connectors for radiation resistance

## Slide 9
Pictures
Copper plates
2 chillers
Staubli connectors outside the box
Heat exchanger

## Slide 10
Pictures
Dividers

## Slide 11
Connectors reference and device list
1 Chillers n°2 : KODIAK RC011G03BG3 ( 4,3 GPM)
1 Chillers n°1 : KODIAK RC006G03BG3 (2,3 GPM)
2 Heat exchangers LYTRON 6320G3SB with fans 10’’ (100236-11)
Copper tube D12- d10
Copper tube D10- d8
Connectors Parker (brass)
https://www.parker.com/literature/Switzerland/Swiss%20PDF%20Files/Catalogue%20Parker%20Legris%20-%20F.pdf
Page 246
List of device in pdf files

## Slide 12
Connectors reference and device list

## Slide 13
Connectors reference and device list