## Slide 1: Thermal balance
Roughly a temperature delta of 38K of each flow channel showing each channel takes half the heat load.
Flat line at inlet not realistic!! Flow needs to be given time to develop outside the cu absorber since temperature does not increase linearly for the 1st 0.1 m of channel.
Temperature at center of fluid channel : Z COORDINATE VS TEMPERATURE
Inlet
180 bend
outlet
There should be no heating (or cooling) at the far end where the piping exits the absorber makes a 180 degree bend and then re-enters the absorber. Should be nearly constant temperature.

## Slide 2
Chart: Expected Temp Profile along length of pipe Temp values are estimates
Tube bend region. No heating/cooling.
Just more mixing occurring?
60cm of heating.
Lower amount of heating occurs. Tube near sides of absorber.
5cm no heating occurs.
Section at start of absorber.
Entrance
Exit