## Slide 1: Hall A Tritium Target Part 1
Dave Meekins
September 15, 2015

## Slide 2: Overview
Part 1: Target Design
  Introduction
  Target system design
    Cell Design
    Vacuum System
    Exhaust system
    Beamline Alterations
    Control system
  Expected Performance
Part 2: Safety systems and failure modes
  Tritium detection and monitoring
  Tritium containment and release
  Response to the prior review

## Slide 3: Design Philosophy
Safety
  Minimize impact from any release scenario
Design shall be simple
Minimize amount of tritium
Do not “handle” tritium
Three layers of containment
  Operations
  Installation/removal
  Transport
Perform well enough to run physics

## Slide 4: CEBAF at JLAB
Continuous e Beam Accelerator
Pair of SRF LINACs with arcs
Delivers beam to 4 Halls
Experiment located in Hall A

## Slide 5: Hall A
Dimensions:
Diameter = 175 ft
Height = ~ 60 ft
Volume
Multiple access ports
include Truck Ramp
HRS: High Res Spectrometers
Target

## Slide 6: Arial View of Hall A

## Slide 7: Target Chamber at Pivot
e Beam
Target/Chamber
Pivot (Hall center)

## Slide 8: Target System
Repurposed Qweak H2 Target
Alter existing Cryostat
  Alter internal piping
  Add two valves
H2 Loop piping and cell removed
Alter cryo piping and instruments
15 K He from ESR
Motion in “X” and “Y” directions
Control system is similar to Hall A cryotarget
“New Construction” pressure system

## Slide 9: Target Ladder
Heat sink cooled by ESR to 40K
Stabilized by heater

## Slide 10: Target Cell
Main Body and Entrance Window
ASTM B209 AL 7075-T651
Valve assy:
SST 316 and 304
1090 Ci of T2 (0.1 g)
~200 psi at 295K
25 cm long
ID of 12.7mm
Volume = 34 cc
Aluminum CF seals

## Slide 11: Cell Cross Section
0.018” wall

## Slide 12: Features
Cell is “sealed”
  No recirculation
  JLAB does not “handle” the T2 gas
Make Al-SST transition with CF flanges
  Many years of successful experience at JLAB
  Work well with H2, He, etc. at low temp < 1K
Modular design
  Can be installed as the final component of the system

## Slide 13: Materials
Main Body and Entrance
  Aluminum 7075-T651 ASTM B209
  Extensive use of this allow for 15 years
  Strong, ductile, hard, non weldable
Seals are Al 1100
Valve assembly
  SST 304/304L Fitting
  Swagelok valve all metal bellows sealed (316L)
  Butt welded ER316L (100% VT in process and RT)

## Slide 14: Materials-2
Al 7075 is unlisted
  Design basis
    for tension
    = 80% of 24 ksi for shear
    = 150% OF 24 ksi bending
Other wetted materials are SST
  304/304L
  316/316L
  ER316L Filler for welds

## Slide 15: Materials 3
Tritium and Hydrogen Compatibility
  Extensive experience with H2
  Beam induced corrosion not expected above 180K (Flower et. al.)
  Beam assisted embrittlement
    Increases fugacity
      Atomic tritium recombines rapidly
    Modeled room fugacity ~3100 psi
    Below threshold for H2 embrittlement
    Many orders of magnitude below He-3 swelling threshold (Louthan)
Test SRNL/SRTE using precracked coupons exposed to 2500 psi T2 underway
  Test follows ASTM 1820 G168 (Precracked Stress Corrosion Testing)
  Samples exposed for 4, 8, 12 months
  M. Morgan, A. Duncan (SRNL)
Tritium is expected to permeate through the cell and seals
  ~0.5 Ci /year very conservative
Calculations given in TGT-CALC-103-010

## Slide 16: Beam Heating
Max beam current min raster
3W in Entrance
3.3 W in Exit
on exit on entrance

## Slide 17: Load Conditions
At room temp
  P = 200 psi
At 40K Beam Off
  Pressure = ~30 psi
  Max Temperature = 40K
Beam On
  Pressure = 36 psi (avg temp of T2 = 53K)
  Max Temperature = ~125K
Cyclic loads
  Cool down/warm up operating cycles = 20
  17800 beam trips (cycles between Beam On and Off)
    150 days, 33% duty factor, 15 trips/hr

## Slide 18: Analysis
Applicable Code ASME B31.3 (2014)
  Section 304.7.2 because of odd geometry
  Used both Hand Calculations and FEA
  Analysis conforming to ASME BPVC VIII D2 with load factors from B31.3 (i.e. 3 instead of 2.4 on P)
Used cyclic screening analysis from D2
  Depth of loads do not require a fatigue analysis
    175 psi pressure cycle (it is closer to 10 psi)
    Considers temperature cycle from 40K to 125K
Design pressure 675 psi
No source of overpressure
Calculations: TGT-CALC-103-002, 7, 8, 12, 13, 14, 15, 17.

## Slide 19: Thermo-Mechanical Model-1
Full temperature load
  Beam on at 20 µA 2x2 mm raster
  Pressure load 400 psi internal (more than 10x)
  Cooling using 40K heat sink
Using an elastic-plastic model
  Model solves and stresses are still below allowable even for over conservative case
  Local plastic failure requirements met
  Analysis not required because of screening analysis

## Slide 20: Thermo-Mechanical Model-2

## Slide 21: Thermo-Mechanical Model-3

## Slide 22: Raster Off
Initial conditions:
  Beam on full raster
  20 microA
Exit window is worst case
Beam spot no raster
  0.150 mm diameter
  Square profile
For high energy beam this spot size is very conservative
Tune shall be checked at each energy
Long term operations at these conditions are forbidden
Typical FSD for raster failure
  < 10 ms
Red curve is upstream section temperature

## Slide 23: Raster Off Time Dependence

## Slide 24: Mech Therm Model of Raster Off

## Slide 25: Commissioning Plan For Target Thickness
Ensure beam profile is correct and BCM/Optics calibrated
Step current 0-20 µA
Collect data T2, H2, D2, He-3
Collect data on Carbon
Develop function for

## Slide 26: Filling/Shipping
Fill at Savannah River Tritium Enterprises SRTE
Different load conditions
  Design pressure of 1000 psi required
  Changing this (e.g. new relief device) not realistic
Thin sections need to be protected during shipping
Solution:
Shipping covers that act as stays

## Slide 27: Filling Covers

## Slide 28: Valve Covers

## Slide 29: Covers on Test Cell

## Slide 30: FEA Covers On

## Slide 31: Filling Cover Analysis
Stayed sections
  D2 Part 5 Elastic-Plastic
  Pressure load = 3000 psi
  Covers bonded on bolted surfaces
  Reaction loads Used to determine bolt loads.
Model solved (local failure checked)
A design pressure of 1000 psi may be assigned in compliance with B31.3

## Slide 32: Summary of Test Results
Multiple hydrotests on components and assemblies
Entrance: Minimum burst above 2900 psi
Main body: Minimum burst above 3400 psi (0.014” section)
Assembly with covers
  Leaked above 4000 psi (seal was damaged)
  Failed above 5500 psi

## Slide 33: Entrance window hydro

## Slide 34: Exit window hydro
0.014” section
Failed above 3400 psi

## Slide 35: Vacuum System
Scattering chamber (standard Hall A)
  1900 liters
  Thin sections for recoil particles (0.014” aluminum)
Two 800 l/s turbos backed by Leybold D60 Mech pump
NEG Pump with backing turbo and mech pumps
Vacuum exhaust part of Tritium Exhaust System and is continuously purged with N2 (1 cfm)
Isolated from upstream beamline vacuum (Be window)
Remote RGA may help diagnose leaks. Serve as leak detector.

## Slide 37: Exhaust System
24” OD 20m tall Stack
12000 cfm blower multispeed
2” pump exhaust
  Run parallel to stack
Stack must also serve as smoke removal
Provides controlled release of secondary and tertiary containment
Pump exhaust is continuous
Blower activated:
  Manual
  Interlocks

## Slide 38: Stack
STACK LOCATION

## Slide 39: Exhaust Routing

## Slide 40: Exhaust Routing in Hall A

## Slide 41: General Requirements
Collect T2 from any release inside Hall A and exhaust in a controlled fashion
Exhaust point shall be 20 m above grade at site boundary
Must serve as part of the smoke removal system (at least 1/3 of the 36000 cfm required)
Must have at least two modes to service hut and to exhaust from Hall A. (500 and 12000 cfm)
Must stack vacuum pump exhaust
  Scattering chamber, dump line, getter system
Makeup air comes from new louvered door at bottom of ramp.
  Prevents overpressure no ramp door.
  Test required for louver system
  Air from outside from smoke removal system on ramp with damper removed

## Slide 42: Transfer Hut
Installed on purpose built platform
  Only in place for installation/removal
  Clear plastic hung from frame
  “Standard” design
Directly attached to chamber adapter
Air is drawn from Hall into hut then chamber and out exhaust system
Air flow across opening 150 fpm ensure T2 containment
Design and fabrication is underway at SRTE
Test installation and air flow in June 2016
Makeup air 500 cfm supplied existing penetrations

## Slide 43: Exhaust Summary
Exhausts secondary (vacuum chamber) and tertiary (Hall A) containment to 20 m stack
Two speed
  ~500 cfm
  12000 cfm
Exhaust system activated
  Vacuum switch failure (interlock)
  Truck ramp lower door (interlock)
  Manual activation (Hall and Counting House) (manual)
  Low speed activated manually for hut (manual)
  T2 monitor (interlock)

## Slide 44: Beamline Alterations
No plans to substantially alter beamline
Upstream beamline shall be isolated by a Be window
  0.008” thick 1” ID.
  Water cooled (3W beam power 25 µA)
  Reentrant (Resides in chamber)
Window is 15 cm from entrance to cell
Densimet collimator 10 cm long installed in tube upstream of window. (W 90% , Cu 8%, Ni 2%)
Maintenance is possible if required.
12 mm thick collimator attached to cells
Collimators should prevent steering error from affecting cell
  Last steering element is 8 m upstream and 2” radius beam pipe.

## Slide 45: Be Isolation Window
0.008” Be window
Cooled by self contained water chiller to 10C
Integrated collimator Densimet

## Slide 46: Be Window Heating
30 µA
2x2 mm raster
Steady state
Chiller set to 10C

## Slide 47: Control System
Use EPICS (distributed I/O)
  Temperature/motion/valve control
  User Interface (UI) through EDM
FSD on high temperature
  Uses interlocks from redundant 718s
UI has integrated alarm handler
EPICS data logger runs continuously
Communications failures Alarm as well

## Slide 48: EPICS Controls
Monitor various temperature and vacuum levels associated with the target system;
Maintain a constant target temperature using an automatic, feedback-driven heater;
Monitor and control the flow of cryogenic helium coolant to the target;
Control both the vertical and horizontal motion of the target cells;
Provide a set of alarms to alert users to off-normal target conditions;
Provide a set of strip charts to track the target performance;
Archive target performance data;
EPICS is not used for safety or integrity

## Slide 49: Cryo-System
ESR 15K He for cooling
Must return ~25K
PID Control heater
  40K
Return mixed with bypass.
Bypass valve on PID
Alarms/interlocks on TS-5 (a/b) and TS-6 (a/b)

## Slide 50: Operations
Dedicated target operator while target is cold
  100% Shift coverage
Target to be moved to “home” position during any access
Operator responds to alarms
  Calls experts if needed
Emergencies are handled by MCC or guards when machine is down.

## Slide 51: Performance Characteristics
½ life for tritium is ~12 .5 years
  5% conversion to He-3 over 1 year run
  Conversion starts immediately
  Fill as close to run date as possible
Fill purity 99.8% T2 +/- 0.02%
Quantity of T2 from
Where is the compressibility of tritium at the fill pressure of 200 psia.
The uncertainties on the quantities above are:
This gives an uncertainty of

## Slide 52: Density Change in Beam

## Slide 53: Density Model
T2 properties derived from H2
  Viscosity, Thermal Conductivity, Heat Capacity, etc.
  Assumed a Real Gas model
  Buoyancy, convection on wall included
Assumed fixed 2.8W from 20 µA and 2x2 mm raster (11 mW/mm linear power density)
  Did not correct heat load for density
Averaged 20% reduction in density along beam path